## Inverter DC matching
Copy Right©Solinteg 30.12.2022
GREEN-Input,ORANGE-Automatic Calculation
PV MODULE PARAMETERS（AT STC） |  |  |  |  | DC INPUT DESIGEN OF INVERTER
NO. | TYPE |  | Value | Unit | NO. | TYPE | Value | Unit | ADVICE
1 | Rated Maximum Power | Pmax | 650 | W | 1 | The maximum quantity of PV modules in PV string | 17 | PCS
2 | Open Circuit Voltage | Voc | 45.3 | V | 2 | The optimal quantity of PV modules in PV string | 16 | PCS
3 | Short Circuit Current | Isc | 18.44 | A | 3 | The minimum quantity of PV modules in PV string | 3.4687 | PCS
4 | Maximum Power Voltage | Vmp | 37.4 | V | 4 | Referenced quantity of PV strings | 4 | String
5 | Maximum Power Current | Imp | 17.39 | A | 5 | Enter adjusted quantity of PV modules in PV string | 15 | PCS
7 | Temperature Coefficient of Isc | αIsc | 0.04 | %/℃ | 6 | Enter adjusted quantity of PV string | 2 | String | PASS
8 | Temperature Coefficient of Voc | βVmp | -0.25 | %/℃ | 7 | Max. input power of inverter | 19.5 | kW | The PV power is too much, it maybe waste, advice reduce the PV modules
9 | Temperature Coefficient of Pmax | γPmp | -0.34 | %/℃ | 8 | Open Circuit Voltage of PV string | 738.9562 | V | PASS
[5 empty] | 9 | Min. Voltage of PV string | 518.925 | V | PASS
LOCAL TEMPERATURE
NO. | TYPE |  | Value | Unit
1 | Local maximum temperature | Tmax | 55 | ℃
2 | Local minimum temperature | Tmin | -10 | ℃
Choose Inverter Model
MHT-4K-25
NO. | TYPE | Value |  | Unit
1 | Rated DC Input Voltage | 620 |  | V
2 | Max. DC Input Voltage | 950 |  | V
3 | Full Power MPPT Voltage Range | 120 | 850 | V
4 | No. of MPP Trackers | 2
5 | No. of DC Inputs | 4
6 | Max. Output Power | 4.4 |  | kW

## PV array shadow distance
Shadow distance of PV array
NO. | TYPE |  | Value | Unit | Remark
1 | The length of the inclined PV array | L | 2000 | mm
2 | Tilt Angle of PV array | β | 30 | °
3 | Local latitude | φ | 30 | °
4 | Distance between front and rear arrays | D | 3576.3067 | mm

## AC Cable loss
Single-phase AC cable loss calculation
NO. | Type | Value | Unit | Remark
1 | Voltage | 230 | V | The local standard voltage
2 | Power | 6 | kW | The power running on the cable
3 | Environment temperature | 45 | ℃ | The maximum environment temperature
4 | AC cable length | 30 | m | Inverter output AC cable length
5 | AC cable specification | 1 | mm2 | Sectional cross sectional area of AC cable
6 | Number of cables in parallel | 1 |  | If multiple cables are used in parallel, fill in the corresponding number
7 | Standard DC resistance | 18.1 | Ω/km | Autocomputed value
8 | AC cable resistance | 0.59624 | Ω | Autocomputed value
9 | AC cable voltage drop | 15.554 | V | Autocomputed value
Three-phase AC cable loss calculation
NO. | Type | Value | Unit | Remark
1 | Voltage | 400 | V | The local standard voltage
2 | Power | 200 | kW | The power running on the cable
3 | Environment temperature | 45 | ℃ | The maximum environment temperature
4 | AC cable length | 250 | m | Inverter output AC cable length
5 | AC cable specification | 50 | mm2 | Sectional cross sectional area of AC cable
6 | Number of cables in parallel | 1 |  | If multiple cables are used in parallel, fill in the corresponding number
7 | Standard DC resistance | 0.387 | Ω/km | Autocomputed value
8 | AC cable resistance | 0.10624 | Ω | Autocomputed value
9 | AC cable voltage drop | 53.1176 | V | Autocomputed value

## Economic efficiency calculation
Calculation of generating capacity and income of PV power station for self-use
NO. | Type | Value | Unit | Remark | Year | Total | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25
1 | PV power | 5 | kWp |  | Cost | 15000 | 1: 15000
2 | PV power station cost | 15000 | dollar | Local currency unit. | Power generation | 137695.0064 | 5880 | 5847.66 | 5815.4979 | 5783.5126 | 5751.7033 | 5720.0689 | 5688.6086 | 5657.3212 | 5626.206 | 5595.2618 | 5564.4879 | 5533.8832 | 5503.4468 | 5473.1779 | 5443.0754 | 5413.1385 | 5383.3662 | 5353.7577 | 5324.312 | 5295.0283 | 5265.9057 | 5236.9432 | 5208.14 | 5179.4952 | 5151.008
3 | Initial annual generated energy | 6000 | kWh | Calculated by PVsyst or empirically estimated, or the website below. | Generating income | 72978.3534 | 3116.4 | 3099.2598 | 3082.2139 | 3065.2617 | 3048.4028 | 3031.6365 | 3014.9625 | 2998.3802 | 2981.8892 | 2965.4888 | 2949.1786 | 2932.9581 | 2916.8268 | 2900.7843 | 2884.83 | 2868.9634 | 2853.1841 | 2837.4916 | 2821.8854 | 2806.365 | 2790.93 | 2775.5799 | 2760.3142 | 2745.1325 | 2730.0342
4 | PV modules degradation in the first year | 2% | % | Refer to PV module specifications, if it is linear degradation，The first year is the same as every year after that. | Net cash flow | 57978.3534 | -11883.6 | 3099.2598 | 3082.2139 | 3065.2617 | 3048.4028 | 3031.6365 | 3014.9625 | 2998.3802 | 2981.8892 | 2965.4888 | 2949.1786 | 2932.9581 | 2916.8268 | 2900.7843 | 2884.83 | 2868.9634 | 2853.1841 | 2837.4916 | 2821.8854 | 2806.365 | 2790.93 | 2775.5799 | 2760.3142 | 2745.1325 | 2730.0342
5 | Annual degradation thereafter | 0.55% | % |  | Accumulative net cash flow |  | -11883.6 | -8784.3402 | -5702.1263 | -2636.8646 | 411.5381 | 3443.1747 | 6458.1372 | 9456.5174 | 12438.4066 | 15403.8954 | 18353.0739 | 21286.032 | 24202.8589 | 27103.6431 | 29988.4731 | 32857.4365 | 35710.6206 | 38548.1122 | 41369.9976 | 44176.3626 | 46967.2926 | 49742.8725 | 52503.1867 | 55248.3191 | 57978.3534
6 | Project operation time | 25 | year |  | Internal rate of return (IRR) | 25.43%
7 | Prices of self-use | 0.53 | dollar/kWh | The price and proportion of PV power generation that is consumed locally by the user's load and not feed into the public grid. | Pay back period | 4.865 | 1 | 1 | 1 | 1 | 0.865 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | Proportion of self-use | 100% | %
9 | Price of feed into public grid | 0 | dollar/kWh | Areas where feed into public is not allowed, enter 0.
10 | Comprehensive price of PV power | 0.53 | doller/kWh
11 | Initial annual income | 3180 | dollar/year
12 | Internal rate of return (IRR) | 25.43% | %
13 | Pay back period | 4.865 | year
Please refer to this website for Initial annual generated energy |  |  |  | https://globalsolaratlas.info/map

## 逆变器参数 (hidden)
| Rated DC Input Voltage | Max. DC Input Voltage | Full Power MPPT Voltage Range |  | No. of MPP Trackers | No. of DC Inputs | Max. Output Power
MHS-3K-30 | 360 | 600 | 100 | 500 | 1 | 1 | 3.3
MHS-3.6K-30 | 360 | 600 | 100 | 500 | 1 | 1 | 3.96
MHS-4.2K-30 | 360 | 600 | 100 | 500 | 2 | 4 | 4.6
MHS-5K-30 | 360 | 600 | 100 | 500 | 2 | 4 | 5.5
MHS-6K-30 | 360 | 600 | 100 | 500 | 2 | 4 | 6.6
MHS-8K-30 | 360 | 600 | 100 | 500 | 2 | 4 | 8
MHT-4K-25 | 620 | 950 | 120 | 850 | 2 | 4 | 4.4
MHT-5K-25 | 620 | 950 | 120 | 850 | 2 | 4 | 5.5
MHT-6K-25 | 620 | 950 | 120 | 850 | 2 | 4 | 6.6
MHT-8K-25 | 620 | 950 | 120 | 850 | 2 | 4 | 8.8
MHT-10K-25 | 620 | 950 | 120 | 850 | 2 | 4 | 11
MHT-12K-25 | 620 | 950 | 120 | 850 | 2 | 4 | 13.2
MHT-10K-40 | 620 | 950 | 200 | 850 | 2 | 4 | 11
MHT-12K-40 | 620 | 950 | 200 | 850 | 2 | 4 | 13.2
MHT-15K-40 | 620 | 950 | 200 | 850 | 2 | 4 | 16.5
MHT-20K-40 | 620 | 950 | 200 | 850 | 2 | 4 | 22
MHT-25K-100 | 620 | 850 | 200 | 850 | 4 | 8 | 27.5
MHT-30K-100 | 620 | 850 | 200 | 850 | 4 | 8 | 33
MHT-36K-100 | 620 | 850 | 200 | 850 | 4 | 8 | 39.6
MHT-40K-100 | 620 | 850 | 200 | 850 | 4 | 8 | 44
MHT-50K-100 | 620 | 850 | 200 | 850 | 4 | 8 | 55

## 直流电阻 (hidden)
电缆20℃最大电阻Ω/Km
截面 | 单芯和多芯用第1种实芯导体 |  |  | 单芯和多芯用第2种实芯导体 |  |  | 单芯和多芯用第5种实芯导体 |  | 单芯和多芯用第5种实芯导体
| 铜（不镀金属） | 铜（镀金属） | 铝 | 铜（不镀金属） | 铜（镀金属） | 铝 | 铜（不镀金属） | 铜（镀金属） | 铜（不镀金属） | 铜（镀金属）
0.5 | 36 | 36.7 | / | 36 | 36.7 | / | 39 | 40.1 | 39 | 40.1
0.75 | 24.5 | 24.8 | / | 24.5 | 24.8 | / | 26 | 26.7 | 26 | 26.7
1 | 18.1 | 18.2 | / | 18.1 | 18.2 | / | 19.5 | 20 | 19.5 | 20
1.5 | 12.1 | 12.2 | 18.1 | 12.1 | 12.2 | / | 13.3 | 13.7 | 13.3 | 13.7
2.5 | 7.41 | 7.56 | 12.1 | 7.41 | 7.56 | / | 7.98 | 8.21 | 7.98 | 8.21
4 | 4.61 | 4.7 | 7.41 | 4.61 | 4.7 | 7.41 | 4.95 | 5.09 | 4.95 | 5.09
6 | 3.08 | 3.11 | 4.61 | 3.08 | 3.11 | 4.61 | 3.3 | 3.39 | 3.3 | 3.39
10 | 1.83 | 1.84 | 3.08 | 1.83 | 1.84 | 3.08 | 1.91 | 1.95 | 1.91 | 1.95
16 | 1.15 | 1.16 | 1.91 | 1.15 | 1.16 | 1.91 | 1.21 | 1.24 | 1.21 | 1.24
25 | 0.727 | 0.734 | 1.2 | 0.727 | 0.734 | 1.2 | 0.78 | 0.795 | 0.78 | 0.798
35 | 0.524 | 0.529 | 0.868 | 0.524 | 0.529 | 0.868 | 0.554 | 0.565 | 0.554 | 0.565
50 | 0.387 | 0.391 | 0.641 | 0.387 | 0.391 | 0.641 | 0.386 | 0.393 | 0.386 | 0.393
70 | 0.268 | 0.27 | 0.443 | 0.268 | 0.27 | 0.443 | 0.272 | 0.277 | 0.272 | 0.277
95 | 0.193 | 0.195 | 0.32 | 0.193 | 0.195 | 0.32 | 0.206 | 0.21 | 0.206 | 0.21
120 | 0.153 | 0.154 | 0.253 | 0.153 | 0.154 | 0.253 | 0.161 | 0.164 | 0.161 | 0.164
150 | 0.124 | 0.126 | 0.206 | 0.124 | 0.126 | 0.206 | 0.129 | 0.132 | 0.129 | 0.132
185 | 0.0991 | 0.1 | 0.164 | 0.0991 | 0.1 | 0.164 | 0.106 | 0.108 | 0.106 | 0.108
240 | 0.0754 | 0.0762 | 0.125 | 0.0754 | 0.0762 | 0.125 | 0.0801 | 0.0817 | 0.0801 | 0.0817
300 | 0.0601 | 0.0607 | 0.1 | 0.0601 | 0.0607 | 0.1 | 0.0641 | 0.0654 | 0.0641 | 0.0654
400 | 0.047 | 0.0475 |  | 0.047 | 0.0475 | 0.0778 | 0.0495 | 0.0495 | 0.0495 | 0.0495
500 | 0.0366 | 0.0369 |  | 0.0366 | 0.0369 | 0.0605 | 0.0391 | 0.0391 | 0.0391 | 0.0391
630 | 0.0283 | 0.0286 |  | 0.0283 | 0.0286 | 0.0469 | 0.0287 | 0.0292 | 0.0287 | 0.0292
800 | 0.0221 | 0.0224 |  | 0.0221 | 0.0224 | 0.0369
1000 | 0.0176 | 0.0177 |  | 0.0176 | 0.0177 | 0.0291